## Sheet1
Modify list | 1.0x34a and 0x34b register for battery temperture and Charger's DAB transformer temperature. 2.Add 0xde register named 'Battery Health', means the health of battery. 3.add a value for allow solar power max ,and feed in to grid(register 0x120).
Holding Register (Read/ Write)
Variable | W (Write) /R (Read) | Decription | Unit | Value Type | Register | Length | User | Ensure
UnlockCommand | W | Allow write to register after unlocking except 0x10 write remote control command | 1 | Uint16 | 0x00 | 1 | Solo | 1919(0x077F)
SeriesNumber | R/W | 16Chars，MSB=SN[16], Inverter serial number | 16Char | Uint16 | 0x01 | 8 | Solo
FactoryName | R | 16Chars，MSB=SN[16], Factory name | 16Char | Uint16 | 0x09 | 8 | Solo
ModuleName | R | 16Chars，MSB=SN[16], Module name | 16Char | Uint16 | 0x11 | 8 | Solo
Machine_Type | R | Machine type |  | Uint16 | 0x19 | 1 | Solo
MyAddress | R/W | machine address (Reserved) | 1 | Uint16 | 0x1a | 1 | Solo
Language | R/W | Langage 0:English 1:German | 0/1 | Uint16 | 0x1b | 1 | Solo
IP Method | R/W | 0:DHCP Method 1:Manual Method | 0/1 | Uint16 | 0x1c | 1 | Solo
Machine switch | R | MSB: software switch; 1=ON;0=OFF LSB: hardware switch:1=ON;0=OFF |  | Uint16 | 0x1d | 1 | Solo
Password | R |  |  | Uint16 | 0x1e | 1 | Solo
Safety | R/W | safety type 0: VDE0126 1: ARN4105 2: AS4777 3: NZS4777 4: C10/11 5: OVE/ONORME8001 6: EN50438_NL 7: EN50438_DK 8: CEB 9: CEI021R 10:NRS097 11: VDE0126_Greece 12: UTE_C15_712 13:IEC61727 14:G98 15:VDE0126_Grece_Cont inent 16: France_VFR2014 17:PEA 18:MEA |  | Uint16 | 0x1f | 1 | Solo
PvConnectionMode | R/W | Solar panel input mode： 0：No Solar Input 1：Comm (Two strings of panels connected in parallel) 2：multi(Two strings of panels connected in parallel independent) |  | Uint16 | 0x20 | 1 | Solo
VpvStart | R/W | Launch voltge threshold | 0.1V | Uint16 | 0x21 | 1 | Solo
TimeStart | R/W | Launch wait time | 1s | Uint16 | 0x22 | 1 | Solo
VpvHighStop | R/W | Input high voltage protect threshold | 0.1V | Uint16 | 0x23 | 1 | Solo
VpvLowStop | R/W | Input low voltage stop thershold | 0.1V | Uint16 | 0x24 | 1 | Solo
VacMinProtect | R/W | allowed minimum grid voltage | 0.1V | Uint16 | 0x25 | 1 | Solo
VacMaxProtect | R/W | allowed maximum grid voltage | 0.1V | Uint16 | 0x26 | 1 | Solo
FacMinProtect | R/W | allowed minimum grid frequency | 0.01Hz | Uint16 | 0x27 | 1 | Solo
FacMaxProtect | R/W | allowed maximum grid frequency | 0.01Hz | Uint16 | 0x28 | 1 | Solo
VacMinSlowProtect | R/W | grid undervoltage protect value | 0.1V | Uint16 | 0x29 | 1 | Solo
VacMaxSlowProtect | R/W | grid overvoltage protect value | 0.1V | Uint16 | 0x2a | 1 | Solo
FacMinSlowProtect | R/W | grid underfrequency protect value | 0.01HZ | Uint16 | 0x2b | 1 | Solo
FacMaxSlowProtect | R/W | grid overfrequency protect value | 0.01HZ | Uint16 | 0x2c | 1 | Solo
Grid10MinAvgProtect | R/W | 10minutes over voltage protect | 0.1V | Uint16 | 0x2d | 1 | Solo
wTimeVacMin_FastAdj | R/W | allowed minimum grid voltage protect fast time | 1ms | Uint16 | 0x2e | 1 | Solo
wTimeVacMax_FastAdj | R/W | allowed maximum grid voltage protect fast time | 1ms | Uint16 | 0x2f | 1 | Solo
wTimeFacMin_FastAdj | R/W | allowed minimum grid Freq protect fast time | 1ms | Uint16 | 0x30 | 1 | Solo
wTimeFacMax_FastAdj | R/W | allowed maximum grid Freq protect fast time | 1ms | Uint16 | 0x31 | 1 | Solo
wTimeVacMin_SlowAdj | R/W | allowed minimum grid voltage protect slow time | 1ms | Uint16 | 0x32 | 1 | Solo
wTimeVacMax_SlowAdj | R/W | allowed maximum grid voltage protect slow time | 1ms | Uint16 | 0x33 | 1 | Solo
wTimeFacMin_SlowAdj | R/W | allowed minimum grid Freq protect slow time | 1ms | Uint16 | 0x34 | 1 | Solo
wTimeFacMax_SlowAdj | R/W | allowed maximum grid Freq protect slow time | 1ms | Uint16 | 0x35 | 1 | Solo
DciLimits | R/W | DC injection limit value for level 1 | 1mA | Uint16 | 0x36 | 1 | Solo
DciLimits2 | R/W | DC injection limit value for level 2 | 1mA | Uint16 | 0x37 | 1 | Solo
DciProtectTime | R/W | Time for DC injection limit value for level 1 | ms | Uint16 | 0x38 | 1 | Solo
DciProtectTime2 | R/W | Time for DC injection limit value for level 2 | ms | Uint16 | 0x39 | 1 | Solo
PowerLimitsPercent | R/W | output power limits precent | 0~100 | Uint16 | 0x3a | 1 | Solo
FreqSetPoint | R/W | Over Frequency drop output set point | 0.01Hz | Uint16 | 0x3b | 1 | Italy/AU
FreqDroopRate | R/W | drop output slope | 1% | Uint16 | 0x3c | 1 | Italy/AU
FreDroopDelayTime | R/W | FreDroopDelayTime | ms | Uint16 | 0x3d | 1 | Italy/AU
PowerfactorMode | R/W | Power factor Mode | 1 | Uint16 | 0x3e | 1 | Solo
PowerfactorData | R/W | Power factor data | 0.01 | Uint16 | 0x3f | 1 | Solo | Set PowerfactorMode=1 means Over(Leading) Mode Set PowerfactorMode=2 means Under(Lagging) Mode Then set this value to change the size of the cos value
UpperLimit | R/W | overexcite limits | 0.01 | Uint16 | 0x40 | 1 | Italy/AU
LowerLimit | R/W | underexcite limits | 0.01 | Uint16 | 0x41 | 1 | Italy/AU
PowerLow | R/W | power ratio change upper limits | 0.01 | Uint16 | 0x42 | 1 | Italy/AU
PowerUp | R/W | power ratio change lower limits | 0.01 | Uint16 | 0x43 | 1 | Italy/AU
Connect Time | R/W | Connect time when first time connect grid | 1s | Uint16 | 0x44 | 1 | Italy/AU
QuVrateLow | R/W | Q(U) curve low set point | 1% | Uint16 | 0x45 | 1 | Italy/AU
PfLockInPoint | R/W | Set Power Factor parameter | 105~110 | Uint16 | 0x46 | 1 | Italy/AU
PfLockOutPoint | R/W | Set Power Factor parameter | 98~90 | Uint16 | 0x47 | 1 | Italy/AU
SelfTestStep | R/W | 1 means start 8 means success Self test result | 1~8 | Uint16 | 0x48 | 1 | Italy Auto Test Only
SelfTestOvpValue | R | Overvoltage value | 0.1V | Uint16 | 0x49 | 1 | Italy Auto Test Only
SelfTestOvpTime | R | Overvoltage time | 1MS | Uint16 | 0x4a | 1 | Italy Auto Test Only
SelfTestUvpValue | R | Undervoltage value | 0.1V | Uint16 | 0x4b | 1 | Italy Auto Test Only
SelfTestUvpTime | R | Undervoltage time | 1MS | Uint16 | 0x4c | 1 | Italy Auto Test Only
SelfTestOfpValue | R | Overfrequency value | 0.01Hz | Uint16 | 0x4d | 1 | Italy Auto Test Only
SelfTestOfpTime | R | Overfrequency time | 1MS | Uint16 | 0x4e | 1 | Italy Auto Test Only
SelfTestUfpValue | R | Underfrequency value | 0.01Hz | Uint16 | 0x4f | 1 | Italy Auto Test Only
SelfTestUfpTime | R | Under frequency time | 1MS | Uint16 | 0x50 | 1 | Italy Auto Test Only
SelfTestOvp10mAvgVal | R | Over voltage of self-test | 0.1V | Uint16 | 0x51 | 1 | Italy Auto Test Only
SelfTestOvp10mAvgTime | R | Over voltage time of self-test | 1ms | Uint16 | 0x52 | 1 | Italy Auto Test Only
SelfTestOfpVal_Restric tive | R | Over frequency of self-test | 0.01Hz | Uint16 | 0x53 | 1 | Italy Auto Test Only
SelfTestOfpTime_Restrictive | R | Over frequency time of self-test | ms | Uint16 | 0x54 | 1 | Italy Auto Test Only
SelfTestUfpVal_Restric tive | R | Under frequency of self-test | 0.01Hz | Uint16 | 0x55 | 1 | Italy Auto Test Only
SelfTestUfpTime_Restrictive | R | Under frequency time of self-test | ms | Uint16 | 0x56 | 1 | Italy Auto Test Only
wExt_SetChargerPower | R/W | when the work mode is "External Use",the Charger's power controlled outside device.Range: +3000(charge) to -3000(discharge) | W | Int16 | 0x57 | 1 | Solo | SolarChargerUseMode=2:External Use
wExt_SetSolarPower | R/W | when the work mode is "External Use",the Solar's power controlled outside device.Range:0 to 4000 | W | Int16 | 0x58 | 1 | Solo | SolarChargerUseMode=3:External Use
PowerManagerConfigData | R/W | PowerManagerConfigData |  | Uint16 | 0x59 | 80 | Italy Only
PowerManagerEnable | R/W | PowerManagerEnable |  | Uint16 | 0xa9 | 1 | Italy Only
FirmwareVersion_Invert erMaster | R | FirmwareVersion_InverterMaster | 1 | Uint16 | 0xaa | 1 | Solo
FirmwareVersion_Invert erSlave | R | FirmwareVersion_InverterSlave | 1 | Uint16 | 0xab | 1 | Solo
FirmwareVersion_Charger1 Master | R | Firmware Version of Charger1 | 1 | Uint16 | 0xac | 1 | Solo
FirmwareVersion_Charger1 Slave | R | Firmware Version of Charger1 Slave | 1 | Uint16 | 0xad | 1 | Solo
FirmwareVersion_Charger2 Master | R | Firmware Version of Charger3 | 1 | Uint16 | 0xae | 1 | No Use
FirmwareVersion_Charger2 Slave | R | Firmware Version of Charger4 | 1 | Uint16 | 0xaf | 1 | No Use
FirmwareVersion_Manager | R | Firmware Version of Manager | 1 | Uint16 | 0xb0 | 1 | Solo
wFirmwareVersion_Protocol | R | Firmware Version of Protocol |  | Uint16 | 0xb1 | 1 | Solo
ItalySelftestStart | W | 1:start 0:stop |  | Uint16 | 0xb2 | 1 | Italy Auto Test Only
RTC-Seconds | R | Second of Clock inside the machine |  | Uint16 | 0xb3 | 1 | Solo
RTC-Minutes | R | Minute of Clock inside the machine |  | Uint16 | 0xb4 | 1 | Solo
RTC-Hours | R | Hour of Clock inside the machine |  | Uint16 | 0xb5 | 1 | Solo
RTC-Days | R | Days of Clock inside the machine |  | Uint16 | 0xb6 | 1 | Solo
RTC-Months | R | Months of Clock inside the machine |  | Uint16 | 0xb7 | 1 | Solo
RTC-Years | R | Years of Clock inside the machine |  | Uint16 | 0xb8 | 1 | Solo
SolarChargerUseMode | R/W | SolarChargerUseMode: 0:Self use mode 1:ForceTimeUse 2:External Use 3:Backup Use 4:FFR Use 5:Remote control mode |  | Uint16 | 0xb9 | 1 | Solo
Allow_Grid_Charge | R/W | Is Charge from Grid allowed 0 (forbidden) 1 (period1 allow） 2 (period2 allow) 3 (both allow) |  | Uint16 | 0xba | 1 | Solo | SolarChargerUseMode=1:ForceTimeUse
Export control factory limit | R/W | Export control factory limit | 1W | Uint16 | 0xbb | 1 | Only For Produte
Export control user limit | R/W | Export control user limit | 1W | Uint16 | 0xbc | 1 | Solo
EPS_Mute | R/W | EPS Mute | 0(off) 1(on) | Uint16 | 0xbd | 1 | Solo
EPS Frequency | R/W | EPS Mode The Voltage Out Frequency | 0(50Hz) 1(60Hz | Uint17 | 0xbe | 1 | Solo
ChargerStartTime1_Hours | R/W | Start time of charging period 1 in ForceTime Use mode of Hours | 0-23 | Uint16 | 0xbf | 1 | Solo | SolarChargerUseMode=1:ForceTimeUse
ChargerStartTime1_Minutes | R/W | Start time of charging period 1 in ForceTime Use mode of Minutes | 0-59 | Uint16 | 0xc0 | 1 | Solo | SolarChargerUseMode=1:ForceTimeUse
ChargerEndTime1_Hours | R/W | End time of charging period 1 in ForceTime Use mode of Hours | 0-23 | Uint16 | 0xc1 | 1 | Solo | SolarChargerUseMode=1:ForceTimeUse
ChargerEndTime1_Minutes | R/W | End time of charging period 1 in ForceTime Use mode of Minutes | 0-59 | Uint16 | 0xc2 | 1 | Solo | SolarChargerUseMode=1:ForceTimeUse
DischargerStartTime1_Hours | R/W | Start time of discharging period 1 in ForceTime Use mode of Hours of Hours | 0-23 | Uint16 | 0xc3 | 1 | Solo | SolarChargerUseMode=1:ForceTimeUse
DischargerStartTime1_Minutes | R/W | Start time of discharging period 1 in ForceTime Use mode of Hours of Minutes | 0-59 | Uint16 | 0xc4 | 1 | Solo | SolarChargerUseMode=1:ForceTimeUse
DischargerEndTime1_Hours | R/W | End time of discharging period 1 in ForceTime Use mode of Hours of Hours | 0-23 | Uint16 | 0xc5 | 1 | Solo | SolarChargerUseMode=1:ForceTimeUse
DischargerEndTime1_Minutes | R/W | End time of discharging period 1 in ForceTime Use mode of Hours of Minutes | 0-59 | Uint16 | 0xc6 | 1 | Solo | SolarChargerUseMode=1:ForceTimeUse
ChargerStartTime2_Hours | R/W | Start time of charging period 2 in ForceTime Use mode of Hours | 0-23 | Uint16 | 0xc7 | 1 | Solo | SolarChargerUseMode=1:ForceTimeUse
ChargerStartTime2_Minutes | R/W | Start time of charging period 2 in ForceTime Use mode of Minutes | 0-59 | Uint16 | 0xc8 | 1 | Solo | SolarChargerUseMode=1:ForceTimeUse
ChargerEndTime2_Hours | R/W | End time of charging period 2 in ForceTime Use mode of Hours | 0-23 | Uint16 | 0xc9 | 1 | Solo | SolarChargerUseMode=1:ForceTimeUse
ChargerEndTime2_Minutes | R/W | End time of charging period 2 in ForceTime Use mode of Minutes | 0-59 | Uint16 | 0xca | 1 | Solo | SolarChargerUseMode=1:ForceTimeUse
DischargerStartTime2_Hours | R/W | Start time of discharging period 2 in ForceTime Use mode of Hours of Hours | 0-23 | Uint16 | 0xcb | 1 | Solo | SolarChargerUseMode=1:ForceTimeUse
DischargerStartTime2_Minutes | R/W | Start time of discharging period 2 in ForceTime Use mode of Hours of Minutes | 0-59 | Uint16 | 0xcc | 1 | Solo | SolarChargerUseMode=1:ForceTimeUse
DischargerEndTime2_Hours | R/W | End time of discharging period 2 in ForceTime Use mode of Hours of Hours | 0-23 | Uint16 | 0xcd | 1 | Solo | SolarChargerUseMode=1:ForceTimeUse
DischargerEndTime2_Minutes | R/W | End time of discharging period 2 in ForceTime Use mode of Hours of Minutes | 0-59 | Uint16 | 0xce | 1 | Solo | SolarChargerUseMode=1:ForceTimeUse
frqprotectrestrictive | R/W | 0/1 |  | Uint16 | 0xcf | 1 | Italy/AU
Reserved |  |  |  | Uint16 | 0xd0 | 5 | No Use
BatteryNum | R | Battery number |  | Uint16 | 0xd5 | 1 | Solo
Battery1_MinCapcity | R | To set te value of minimum battery capacity | 1% | Uint16 | 0xd6 | 1 | Solo
Battery1Type | R/W | battery type 0:lead acid 1:lithium |  | Uint16 | 0xd7 | 1 | Solo
Battery1_ChargeCutVoltage | R/W | battery charge cut off voltage | 0.01 | Uint16 | 0xd8 | 1 | Solo
Battery1_DischargeCutVoltage | R/W | battery discharge cut off voltage | 0.01 | Uint16 | 0xd9 | 1 | Solo
Battery1_ChargeMaxCurrent | R/W | Battery charge Maximun Current | 0.01 | Uint16 | 0xda | 1 | Solo
Battery1_DischargeMaxCurrent | R/W | Battery Discharge Maximun Current | 0.01 | Uint16 | 0xdb | 1 | Solo
wBattery1_absorpt_voltage | R/W | Battery Qian charge_absorption_voltage | 0.01 | Uint16 | 0xdc | 1 | Only For Lead-Acid
wBattery1_wEpsDischargeVolt | R/W | Battery eps discharge voltage | 0.01 | Uint16 | 0xdd | 1 | Only For Lead-Acid
wBattery1_healthy | R | Battery healthy | 1% | Uint16 | 0xde | 1 | Solo
Charge1_MinCapcity | R/W | Idle MinCapcity | 1% | Uint16 | 0xdf | 1 | No Use
Bat_awaking | R/W | Cannot start when battery power is low,set 1 for awaking now | 0/1 | uint16 | 0xe0 | 1 | Solo
wBattery1_VendorCode | R/W | Protocal for battery BMS 0:NA 1:LS 2:LG 3:PN | 0/1 | uint16 | 0xe1 | 1 | Solo
Reserved |  |  |  | Uint16 | 0xe2 | 1 | No Use
Battery2_MinCapcity | R | battery Min Capcity | 1% | Uint16 | 0xe3 | 1 | No Use
Battery2Type | R/W | battery type 0:lead acid 1:lithium |  | Uint16 | 0xe4 | 1 | No Use
Battery2_ChargeCutVoltage | R/W | battery charge cut off voltage | 0.01 | Uint16 | 0xe5 | 1 | No Use
Battery2_DischargeCutVoltage | R/W | battery discharge cut off voltage | 0.01 | Uint16 | 0xe6 | 1 | No Use
Battery2_ChargeMaxCurrent | R/W | Battery charge Maximun Current | 0.01 | Uint16 | 0xe7 | 1 | No Use
Battery2_DischargeMaxCurrent | R/W | Battery Discharge Maximun Current | 0.01 | Uint16 | 0xe8 | 1 | No Use
wBattery2_absorpt_voltage | R/W | Battery Qian charge_absorption_voltage | 0.01 | Uint16 | 0xe9 | 1 | No Use
wBattery2_wEpsDischargeVolt | R/W | Battery eps discharge voltage | 0.01 | Uint16 | 0xea | 1 | No Use
wBattery2_healthy | R | Battery healthy | 1% | Uint16 | 0xeb | 1 | No Use
Charge2_MinCapcity | R/W | Idle MinCapcity | 1% | Uint16 | 0xec | 1 | No Use
Charge2_ Bat_awaking | R/W | 1for awaking now | 0/1 | uint16 | 0xed | 1 | No Use
wBattery2_VendorCode | R/W | 0:NA 1:LS 2:LG 3:PN | 0/1 | uint16 | 0xee | 1 | No Use
Reserved |  |  |  | Uint16 | 0xef | 2 | No Use
Battery3_MinCapcity | R | batter Min Capcity | 1% | Uint16 | 0xf1 | 1 | No Use
Battery3Type | R/W | battery type 0:lead acid 1:lithium | — | Uint16 | 0xf2 | 1 | No Use
Battery3_ChargeCutVoltage | R/W | battery charge cut off voltage | 0.01 | Uint16 | 0xf3 | 1 | No Use
Battery3_DischargeCutVoltage | R/W | battery discharge cut off voltage | 0.01 | Uint16 | 0xf4 | 1 | No Use
Battery3_ChargeMaxCurrent | R/W | Battery charge Maximun Current | 0.01 | Uint16 | 0xf5 | 1 | No Use
Battery3_DischargeMaxCurrent | R/W | Battery Discharge Maximun Current | 0.01 | Uint16 | 0xf6 | 1 | No Use
wBattery3_absorpt_voltage | R/W | Battery Qian charge_absorption_voltage | 0.01 | Uint16 | 0xf7 | 1 | No Use
wBattery3_wEpsDischargeVolt | R/W | Battery eps discharge voltage | 0.01 | Uint16 | 0xf8 | 1 | No Use
wBattery3_healthy | R | Battery healthy | 1% | Uint16 | 0xf9 | 1 | No Use
Charge3_MinCapcity | R/W | Idle MinCapcity | 1% | Uint16 | 0xfa | 1 | No Use
Charge3_ Bat_awaking | R/W | 1for awaking now | 0/1 | uint16 | 0xfb | 1 | No Use
wBattery3_VendorCode | R/W | 0:NA 1:LS 2:LG 3:PN | 0/1 | uint16 | 0xfc | 1 | No Use
Reserved |  |  |  | Uint16 | 0xfd | 2 | No Use
Battery4_MinCapcity | R | batter Min Capcity | 1% | Uint16 | 0xff | 1 | No Use
Battery4Type | R/W | battery type 0:lead acid 1:lithium |  | Uint16 | 0x100 | 1 | No Use
Battery4_ChargeCutVoltage | R/W | battery charge cut off voltage | 0.01 | Uint16 | 0x101 | 1 | No Use
Battery4_DischargeCutVoltage | R/W | battery discharge cut off voltage | 0.01 | Uint16 | 0x102 | 1 | No Use
Battery4_ChargeMaxCurrent | R/W | Battery charge Maximun Current | 0.01 | Uint16 | 0x103 | 1 | No Use
Battery4_DischargeMaxCurrent | R/W | Battery Discharge Maximun Current | 0.01 | Uint16 | 0x104 | 1 | No Use
wBattery4_absorpt_voltage | R/W | Battery Qian charge_absorption_voltage | 0.01 | Uint16 | 0x105 | 1 | No Use
wBattery4_wEpsDischargeVolt | R/W | Battery eps discharge voltage | 0.01 | Uint16 | 0x106 | 1 | No Use
wBattery4_healthy | R | Battery healthy | 1% | Uint16 | 0x107 | 1 | No Use
Charge4_MinCapcity | R/W | Idle MinCapcity | 1% | Uint16 | 0x108 | 1 | No Use
Charge4_ Bat_awaking | R/W | 1for awaking now | 0/1 | uint16 | 0x109 | 1 | No Use
wBattery4_VendorCode | R/W | 0:NA 1:LS 2:LG 3:PN | 0/1 | uint16 | 0x10a | 1 | No Use
Reserved |  |  |  | Uint16 | 0x10b | 2 | No Use
MAC Address | R/W | 6Chars，MSB=MAC[5] | 6Chars | Uint16 | 0x10d | 3 | No Use
BackUp_GridChargeFlag | R/W | Apply backup mode to allow energy to be absorbed from the grid | 0/1 | Uint16 | 0x110 | 1 | Solo | SolarChargerUseMode=3:Backup Use
wBackUp_Chr_Start_H | R/W | Start time of charging period 1 in BackUp Use mode of Hours | 1 | Uint16 | 0x111 | 1 | Solo | SolarChargerUseMode=3:Backup Use
wBackUp_Chr_Start_M | R/W | Start time of charging period 1 in BackUp Use mode of Minutes | 1 | Uint16 | 0x112 | 1 | Solo | SolarChargerUseMode=3:Backup Use
wBackUp_Chr_End_H | R/W | End time of charging period 1 in BackUp Use mode of Hours | 1 | Uint16 | 0x113 | 1 | Solo | SolarChargerUseMode=3:Backup Use
wBackUp_Chr_End_M | R/W | End time of charging period 1 in BackUp Use mode of Minutes | 1 | Uint16 | 0x114 | 1 | Solo | SolarChargerUseMode=3:Backup Use
wPFValue | R/W | Reactive power control mode is fixed value mode | Var | Uint16 | 0x115 | 1 | Italy/AU
wCTMeterEnableFlg | R/W | External CT or meter enable setting: 0: Forbidden;1：enable； | 0/1 | Uint16 | 0x116 | 1 | Solo
wFreqOverStart | R/W | FFR function over frequency starting point, range :50-52Hz，Default Value：50.50Hz | 0.01Hz | Uint16 | 0x117 | 1 | Solo | SolarChargerUseMode=4:FFR Use
wFreqOverEnd | R/W | FFR function over-frequency end point, range 50-52Hz Default Value: 52Hz | 0.01Hz | Uint16 | 0x118 | 1 | Solo | SolarChargerUseMode=4:FFR Use
wFreqUnderStart | R/W | FFR function underfrequency starting point, range 48-50Hz Default Value: 49.50Hz | 0.01Hz | Uint16 | 0x119 | 1 | Solo | SolarChargerUseMode=4:FFR Use
wFreqUnderEnd | R/W | FFR function underfrequency end point, range 48-50Hz Default Value: 48Hz | 0.01Hz | Uint16 | 0x11a | 1 | Solo | SolarChargerUseMode=4:FFR Use
wFFR_SOC_Reseved | R/W | FFR function low frequency feedin grid energy reserve, range 10-80%, default value: 30% | 1% | Uint16 | 0x11b | 1 | Solo | SolarChargerUseMode=4:FFR Use
wRemoteChargeSubMode | R/W | 0：Charge，Only from Solar power, does not consume power from Grid 1：Charge Battery to the maximum, from Solar power and consumes energy from Grid 2: the same as 4 3：Discharge, Solar power + Battery power to inverter feed in power to the maximum 4:Charge/Discharge, Solar power + Battery discharge power feed in/comsume grid power (can be set 0x11D) 9: Default, if “remote charge” not be set, Hybrid inverter will work at “self-use” mode |  | Uint16 | 0x11c | 1 | Solo | SolarChargerUseMode=5:Remote control mode
wRemoteChargerPowerSet | R/W | Charge(Comsume fromgrid)Max：-6000； Discharge(feedin toGrid)Max：6000 | W | Int16 | 0x11d | 1 | Solo | SolarChargerUseMode=5:Remote control mode
Reserved |  |  |  |  | 0x11e | 1
Reserved |  |  |  |  | 0x11f | 1
AllowSolarMaxUse | R/W | FFR function the frequecy is lower the point, and need feed in power to grid. If this value is Enable means allow the remain solar power to grid, otherwise not allow the solar power to grid. Disable:0 Enable:1 | 1 | Uint16 | 0x120 | 1 | Solo | SolarChargerUseMode=4:FFR Use
Holding Register (Read Only)
Variable | W (Write) R (Read) | Decription | Unit | Value Type | Register | Lenth
LockState | R | 0:Lock(can't write except Function 0x10 remote control command),2:Unlock(can write register) | -- | Uint16 | 0x300 | 1 | Solo
GridVoltage | R | Grid's Voltage | 0.1V | Uint16 | 0x301 | 1 | Solo
GridCurrent | R | Grid's Current | 0.1V | Int16 | 0x302 | 1 | Solo
GridPower | R | Inverter's output power | 1W | Int16 | 0x303 | 1 | Solo
GridFrequency | R | Grid's Frequency | 0.01Hz | Uint16 | 0x304 | 1 | Solo
PvVoltage1 | R | Voltage of solar input 1 | 0.1V | Uint16 | 0x305 | 1 | Solo
PvVoltage2 | R | Voltage of solar input 2 | 0.1V | Uint16 | 0x306 | 1 | Solo
PvCurrent1 | R | Current of solar input 1 | 0.1A | Uint16 | 0x307 | 1 | Solo
PvCurrent2 | R | Current of solar input 2 | 0.1A | Uint16 | 0x308 | 1 | Solo
Temperature | R | Ambient temperature inside the inverter | 1℃ | Int16 | 0x309 | 1 | Solo
RunMode | R | RunMode: 0: Wait Mode(Waiting for a start condition) 1: Check Mode(Check fault befor on grid) 2:Normal Mode (On grid) 3:Fault Mode (stops working when there is a recoverable failure) 4:Permanent Mode (stops working when there is an unrecoverable failure) 5:Update Mode 6:EPS Mode(Emergency Power Supply When Grid Lost) 7:Self Test Mode(Italy Only) 8:Idel Mode(Reduce standby losses ) | — | Uint16 | 0x30a | 1 | Solo
Powerdc1 | R | Power of solar input 1 | 1W | Uint16 | 0x30b | 1 | Solo
Powerdc2 | R | Power of solar input 2 | 1w | Uint16 | 0x30c | 1 | Solo
TemperFaultValue | R | When the inverter's temperature is over the protect value | 1℃ | Int16 | 0x30d | 1 | Solo
Pv1VoltFaultValue | R | Voltage fault value of solar input 1 | 0.1V | Uint16 | 0x30e | 1 | Solo
Pv2VoltFaultValue | R | Voltage fault value of solar input 2 | 0.1V | Uint16 | 0x30f | 1 | Solo
GfciFaultValue | R | Leakage current fault value | 1mA | Uint16 | 0x310 | 1 | Solo
GridVoltFaultValue | R | Grid‘s voltage fault value | 0.1V | Uint16 | 0x311 | 1 | Solo
GridFreqFaultValueT | R | Grid's frequency fault value | 0.01Hz | Uint16 | 0x312 | 1 | Solo
DciFaultValue | R | DC injection fault value | 1mA | Uint16 | 0x313 | 1 | Solo
TimeCountDown | R | Countdown to Normal state | 1S | Uint16 | 0x314 | 1 | Solo
Reserved |  |  |  | Uint16 | 0x315 | 1 | Solo
feedin_power | R | power to the grid (LSB Receive first and than MSB) | 1W | Int32 | 0x316 | 2 | Solo
feedin_energy | R | energy to the grid (LSB Receive first and than MSB) | 0.01kwh | Uint32 | 0x318 | 2 | No Use
consum_energy | R | energy form the grid (LSB Receive first and than MSB) | 0.01kwh | Uint32 | 0x31a | 2 | No Use
Etoday | R | Day's energy generation when on grid mode | 0.01kwh | Uint16 | 0x31c | 1 | Solo
Reserved |  |  |  | Uint16 | 0x31d |  | No Use
Etotal | R | Total's energy generation when on grid mode | 0.01kwh | Uint32 | 0x31e | 2 | Solo
feedin_power2 | R | power to the grid (LSB Receive first and than MSB) | 1W | Int32 | 0x320 | 2 | No Use
feedin_energy2 | R | energy to the grid (LSB Receive first and than MSB) | 0.01kwh | Uint32 | 0x322 | 2 | No Use
consum_energy2 | R | energy form the grid (LSB Receive first and than MSB) | 0.01kwh | Uint32 | 0x324 | 2 | No Use
Etoday2 | R | Daily Generation 2 | 0.01kwh | Uint16 | 0x326 | 1 | No Use
Reserved |  |  |  | Uint16 | 0X327 | 1 | No Use
Etotal2 | R | Total Energy (Generation) 2 | 0.01kwh | Uint32 | 0x328 | 2 | No Use
EPS_Volt | R | Inverter output voltage value when EPS mode | 0.1V | Uint16 | 0x32A | 1 | Solo
EPS_Current | R | Inverter output cuurent value when EPS mode | 0.1A | Uint16 | 0x32B | 1 | Solo
EPS_Power | R | Inverter output power value when EPS mode | 1VA | Uint16 | 0x32C | 1 | Solo
EPS_Frequency | R | Inverter output frrequency value when EPS mode | 0.01Hz | Uint16 | 0x32D | 1 | Solo
EtodayEPS | R | Today's energy generation when EPS mode | 0.1kwh | Uint16 | 0x32E | 1 | Solo
Reserved |  |  |  | Uint16 | 0x32f | 1 | No Use
EtotalEPS | R | Total's energy generation when EPS mode | 0.1kwh | Uint32 | 0x330 | 2 | Solo
PowerLoad | R | Home Load power | 1W | Uint16 | 0x332 | 1 | Solo
EtodayLoad | R | Energy consumed by home load today | 0.1kwh | Uint16 | 0x333 | 1 | Solo
EtotalLoad | R | total home load consumption | 0.1kwh | Uint32 | 0x334 | 2 | Solo
PvEnergyToday |  | Today's PV energy | 0.1Kwh | Uint16 | 0x336 | 1 | Solo
Reserved |  |  |  | Uint16 | 0x337 | 1 | No Use
PvEnergyTotal | R | PvEnergyTotal (LSB Receive first and than MSB) | 0.1Kwh | Uint32 | 0x338 | 2 | Solo
wCanCommLost | R | Bms connect state |  | Uint16 | 0x33a | 1 | Solo
Reserved |  |  |  | Uint16 | 0x33b | 5 | No Use
InvFaultMessage1 | R | Inverter fault message1 |  | Uint16 | 0x340 | 1 | Solo
InvFaultMessage2 | R | Inverter fault message2 |  | Uint16 | 0x341 | 1 | Solo
InvFaultMessage3 | R | Inverter fault message3 |  | Uint16 | 0x342 | 1 | Solo
InvFaultMessage4 | R | Inverter fault message4 |  | Uint16 | 0x343 | 1 | Solo
Mgr FaultMessage | R | Manage Board's fault message |  | Uint16 | 0x344 | 1 | Solo
chargerNum | R | Number of charger |  | Uint16 | 0x345 | 1 | Solo
BatVoltage_Charge1 | R | Battery's voltage of Charge1 | 0.01V | Int16 | 0x346 | 1 | Solo
BatCurrent_Charge1 | R | Battery's current of Charge1 | 0.01A | Int16 | 0x347 | 1 | Solo
Batpower_Charge1 | R | Battery's power of Charge1 | 1W | Int16 | 0x348 | 1 | Solo
TemperatureBoard_Charge1 | R | PCB board's temperature of Charge1 | 1℃ | Int16 | 0x349 | 1 | Solo
TemperatureBat_Charge1 | R | Battery' charger temperature of Charge1/ Battery's cell temperature of Charge1 | 1℃ | Int16 | 0x34a | 1 | Solo
TemperatureTransformer_Charge1 | R | DAB's transformaer temperature of Charge1 | 1℃ | Int16 | 0x34b | 1 | Solo | The temperature of the phase-shifted full-bridge transformer
BatVoltageFaultValue_Charger1 | R | BatVoltageFaultValue_Charge1 | 0.1V | Uint16 | 0x34c | 1 | No Use
BatCurrentFaultValue_Charge1 | R | BatCurrentFaultValue_ Charge1 | 0.01A | Int16 | 0x34d | 1 | No Use
BoostVoltageFaultValue_Charge1 | R | BoostVoltageFaultValue_Charge1 | 0.1V | Uint16 | 0x34e | 1 | No Use
BoostCurrentFaultValue_Charge1 | R | BoostCurrentFaultValue_ Charge1 | 0.01A | Int16 | 0x34f | 1 | No Use
Capacity_Charge1 | R | Current capacity of Charge1 | 1% | Uint16 | 0x350 | 1 | Solo
Reserved |  |  |  | Uint16 | 0x351 | 1 | No Use
OutputEnergy_Charge1.LSB | R | Output Energy of Charge1(LBS) | 0.1KWh | Uint16 | 0x352 | 1 | Solo
OutputEnergy_Charge1.MSB | R | Output Energy of Charge1(MBS) | 0.1KWh | Uint16 | 0x353 | 1 | Solo
BMS1 warnings | R | Warning message of battery 1 | - | Uint16 | 0x354 | 1 | Solo
Reserved |  |  |  | Uint16 | 0x355 | 1 | No Use
Charger1 FaultMessage1 | R | Charger FaultMessage |  | Uint16 | 0x356 | 1 | Solo
Charger1 FaultMessage2 | R | Charger FaultMessage |  | Uint16 | 0x357 | 1 | Solo
Charger1 FaultMessage3 | R | Charger FaultMessage |  | Uint16 | 0x358 | 1 | Solo
Charger1 FaultMessage4 | R | Charger FaultMessage |  | Uint16 | 0x359 | 1 | Solo
Reserved |  |  |  | Uint16 | 0x35a | 2 | No Use
BatVoltage_Charge2 | R | BatVoltage_Charge2 | 0.01V | Int16 | 0x35c | 1 | No Use
BatCurrent_Charge2 | R | BatCurrent_Charge2 | 0.01A | Int16 | 0x35d | 1 | No Use
Batpower_Charge2 | R | Batpower_Charge2 | 1W | Int16 | 0x35e | 1 | No Use
TemperatureBoard_Charge2 | R | TemperatureBoard_Charge2 | 1℃ | Int16 | 0x35f | 1 | No Use
TemperatureBat_Charge2 | R | TemperatureBat_Charge2 | 1℃ | Int16 | 0x360 | 1 | No Use
TemperatureBoost_Charge2 | R | TemperatureBoost_Charge2 | 1℃ | Int16 | 0x361 | 1 | No Use
BatVoltageFaultValue_Charge2 | R | BatVoltageFaultValue_Charge2 | 0.1V | Uint16 | 0x362 | 1 | No Use
BatCurrentFaultValue_Charge2 | R | BatCurrentFaultValue_Charge2 | 0.01A | Int16 | 0x363 | 1 | No Use
BoostVoltageFaultValue_Charge2 | R | BoostVoltageFaultValue_Charge2 | 0.1V | Uint16 | 0x364 | 1 | No Use
BoostCurrentFaultValue_Charge2 | R | BoostCurrentFaultValue_Charge2 | 0.01A | Int16 | 0x365 | 1 | No Use
Capacity_Charge2 | R | Charge2 capacity | 1% | Uint16 | 0x366 | 1 | No Use
Reserved |  |  |  | Uint16 | 0x367 | 1 | No Use
OutputEnergy_Charge2.LSB | R | OutputEnergy_Charge2 | 0.1KWh | Uint16 | 0x368 | 1 | No Use
OutputEnergy_Charge2.MSB | R | OutputEnergy_Charge2 | 0.1KWh | Uint16 | 0x369 | 1 | No Use
BMS2 warnings | R | BMS2 warning message | - | Uint16 | 0x36A | 1 | No Use
BMS2 warnings back | R | BMS2 warnings back | - | Uint16 | 0x36B | 1 | No Use
Charger2 FaultMessage1 | R | Charger FaultMessage |  | Uint16 | 0x36C | 1 | No Use
Charger2 FaultMessage2 | R | Charger FaultMessage |  | Uint16 | 0x36D | 1 | No Use
Charger2 FaultMessage3 | R | Charger FaultMessage |  | Uint16 | 0x36E | 1 | No Use
Charger2 FaultMessage4 | R | Charger FaultMessage |  | Uint16 | 0x36F | 1 | No Use
Reserved |  |  |  | Uint16 | 0x370 | 2 | No Use
BatVoltage_Charge3 | R | BatVoltage_Charge3 | 0.01V | Int16 | 0x372 | 1 | No Use
BatCurrent_Charge3 | R | BatCurrent_Charge3 | 0.01A | Int16 | 0x373 | 1 | No Use
Batpower_Charge3 | R | Batpower_Charge3 | 1W | Int16 | 0x374 | 1 | No Use
TemperatureBoard_Charge3 | R | TemperatureBoard_Charge3 | 1℃ | Int16 | 0x375 | 1 | No Use
TemperatureBat_Charge3 | R | TemperatureBat_Charge3 | 1℃ | Int16 | 0x376 | 1 | No Use
TemperatureBoost_Charge3 | R | TemperatureBoost_Charge3 | 1℃ | Int16 | 0x377 | 1 | No Use
BatVoltageFaultValue_Charge3 | R | BatVoltageFaultValue_Charge3 | 0.1V | Uint16 | 0x378 | 1 | No Use
BatCurrentFaultValue_Charge3 | R | BatCurrentFaultValue_Charge3 | 0.01A | Int16 | 0x379 | 1 | No Use
BoostVoltageFaultValue_Charge3 | R | BoostVoltageFaultValue_Charge3 | 0.1V | Uint16 | 0x37a | 1 | No Use
BoostCurrentFaultValue_Charge3 | R | BoostCurrentFaultValue_Charge3 | 0.01A | Int16 | 0x37b | 1 | No Use
Capacity_Charge3 | R | Charge3 capacity | 1% | Uint16 | 0x37c | 1 | No Use
Reserved |  |  |  | Uint16 | 0x37d | 1 | No Use
OutputEnergy_Charge3.LSB | R | OutputEnergy_Charge3 | 0.1KWh | Uint16 | 0x37e | 1 | No Use
OutputEnergy_Charge3.MSB | R | OutputEnergy_Charge3 | 0.1KWh | Uint16 | 0x37f | 1 | No Use
BMS3 warnings | R | BMS3 warning message | - | Uint16 | 0x380 | 1 | No Use
BMS3 warnings back | R | BMS3 warnings back message | - | Uint16 | 0x381 | 1 | No Use
Charger3 FaultMessage1 | R | Charger FaultMessage |  | Uint16 | 0x382 | 1 | No Use
Charger3 FaultMessage2 | R | Charger FaultMessage |  | Uint16 | 0x383 | 1 | No Use
Charger3 FaultMessage3 | R | Charger FaultMessage |  | Uint16 | 0x384 | 1 | No Use
Charger3 FaultMessage4 | R | Charger FaultMessage |  | Uint16 | 0x385 | 1 | No Use
Reserved |  |  |  | Uint16 | 0x386 | 2 | No Use
BatVoltage_Charge4 | R | BatVoltage_Charge4 | 0.01V | Int16 | 0x388 | 1 | No Use
BatCurrent_Charge4 | R | BatCurrent_Charge4 | 0.01A | Int16 | 0x389 | 1 | No Use
Batpower_Charge4 | R | Batpower_Charge4 | 1W | Int16 | 0x38a | 1 | No Use
TemperatureBoard_Charge4 | R | TemperatureBoard_Charge4 | 1℃ | Int16 | 0x38b | 1 | No Use
TemperatureBat_Charge4 | R | TemperatureBat_Charge4 | 1℃ | Int16 | 0x38c | 1 | No Use
TemperatureBoost_Charge4 | R | TemperatureBoost_Charge4 | 1℃ | Int16 | 0x38d | 1 | No Use
BatVoltageFaultValue_Charge4 | R | BatVoltageFaultValue_Charge4 | 0.1V | Uint16 | 0x38e | 1 | No Use
BatCurrentFaultValue_Charge4 | R | BatCurrentFaultValue_Charge4 | 0.01A | int16 | 0x38f | 1 | No Use
BoostVoltageFaultValue_Charge4 | R | BoostVoltageFaultValue_Charge4 | 0.1V | Uint16 | 0x390 | 1 | No Use
BoostCurrentFaultValue_Charge4 | R | BoostCurrentFaultValue_Charge4 | 0.01A | Int16 | 0x391 | 1 | No Use
Capacity_Charge4 | R | Charge4 capacity | 1% | Uint16 | 0x392 | 1 | No Use
Reserved |  |  |  | Uint16 | 0x393 | 1 | No Use
OutputEnergy_Charge4.LSB | R | OutputEnergy_Charge4 | 0.1KWh | Uint16 | 0x394 | 1 | No Use
OutputEnergy_Charge4.MSB | R | OutputEnergy_Charge4 | 0.1KWh | Uint16 | 0x395 | 1 | No Use
BMS4 warnings | R | BMS4 warning message | - | Uint16 | 0x396 | 1 | No Use
BMS4 warnings back | R | BMS4 warnings back message | - | Uint16 | 0x397 | 1 | No Use
Charger4 FaultMessage1 | R | Charger FaultMessage |  | Uint16 | 0x398 | 1 | No Use
Charger4 FaultMessage2 | R | Charger FaultMessage |  | Uint16 | 0x399 | 1 | No Use
Charge4 FaultMessage3 | R | Charger FaultMessage |  | Uint16 | 0x39a | 1 | No Use
Charge4 FaultMessage4 | R | Charger FaultMessage |  | Uint16 | 0x39b | 1 | No Use
Reserved | [6 empty] | No Use
DEBUG | R |  |  | int16 | 0x---- | 10
Writable register value table
Variable | W (Write) /R (Read) | Decription | Unit | Value Type | Register | Length
Inverter_Reset_E2 prom | W | Inverter_Reset_E2prom | 1 | Uint16 | 0x00 | 1 | Solo
Inverter_Clear_Hi story | W | Inverter_Clear_History | 1 | Uint16 | 0x01 | 1 | Solo
Clear overload fault | W | Clear overload fault,Write 1 effcet | 1 | Uint16 | 0x02 | 1 | Solo
Reset_Mgr_EE | W | Manager reset: 1:Reset normal configuration 2:Reset all configuration | 1 | Uint16 | 0x03 | 1 | Solo
Reserved |  |  |  | Uint16 |  | 6
Write Multiple Register
Variable | W(Write) /R (Read) | Decription | Unit | Value Type | Register | Length
RTC-Seconds | W | Second of Clock inside the machine | 0-59 | Uint16 | 0x0000- 0x0005 | 6 | Solo
RTC-Minutes | W | Minute of Clock inside the machine | 0-59 | Uint16 |  |  | Solo
RTC-Hours | W | Hour of Clock inside the machine | 0-23 | Uint16 |  |  | Solo
RTC-Days | W | Days of Clock inside the machine | 1~31 | Uint16 |  |  | Solo
RTC-Months | W | Months of Clock inside the machine | 1~12 | Uint16 |  |  | Solo
RTC-Years | W | Years of Clock inside the machine | 0-99 | Uint16 |  |  | Solo
SeriesNumber | W | MSB=SN[13] | 16Char | Uint16 | 0x0006- | 8 | Solo
FactoryName | W | MSB=FactoryName[13] | 16Char | Uint16 | 0x000E- | 8 | Solo
ModuleName | W | MSB=ModuleName[13] | 16Char | Uint16 | 0x0016- | 8 | Solo
IP_Address1 | W | IP_Address1 | 0-255 | Uint16 | 0x001e- 0x0021 | 4 | Solo
IP_Address2 | W | IP_Address2 | 0-255 | Uint16 |  |  | Solo
IP_Address3 | W | IP_Address3 | 0-255 | Uint16 |  |  | Solo
IP_Address4 | W | IP_Address4 | 0-255 | Uint16 |  |  | Solo
SubNetMask1 | W | SubNetMask1 | 0-255 | Uint16 | 0x0022- 0x0025 | 4 | Solo
SubNetMask2 | W | SubNetMask2 | 0-255 | Uint16 |  |  | Solo
SubNetMask3 | W | SubNetMask3 | 0-255 | Uint16 |  |  | Solo
SubNetMask4 | W | SubNetMask4 | 0-255 | Uint16 |  |  | Solo
GateWay1 | W | GateWay1 | 0-255 | Uint16 | 0x0026- 0x0029 | 4 | Solo
GateWay2 | W | GateWay2 | 0-255 | Uint16 |  |  | Solo
GateWay3 | W | GateWay3 | 0-255 | Uint16 |  |  | Solo
GateWay4 | W | GateWay4 | 0-255 | Uint16 |  |  | Solo
PowerManager | W | extern control input config |  | Uint16 | 0x002a- 0x0077 | 80 | Italy/AU
SolarChargerUseMode | W | 0:Self use mode 1:ForceTimeUse 2:External Use 3:Backup Use 4:FFR Use 5:Remote control mode | - | Uint16 | 0x0100- 0x102 | 3 | Solo
wRemoteChargeSubMode | W | refer to register 0x11c |  | Uint16
wRemoteChargerPowerSet | W | refer to register 0x11d | W | Int16
Reguration Parameterextern Settings Table
Variable | W (Write) R (Read) | Decription | Unit | Value Type | Register | Length
exportlimit_EE | W/R | Exportlimit in eeprom |  | Int32 | 0x00 | 2 | AU/NZ
Factorylimit_EE | W/R | Factorylimit in eeprom |  | Int32 | 0x02 | 2 | AU/NZ
ExportPowerLimitByInv | W/R | ExportPowerLimitByInv |  | Int16 | 0x04 | 1 | AU/NZ
ChargePowerLimitByInv | W/R | ChargePowerLimitByInv |  | Int16 | 0x05 | 1 | AU/NZ
exportlimit | W/R | Exportlimit power |  | Int32 | 0x06 | 2 | AU/NZ
ConsGridlimit | W/R | ConsGridlimit power |  | Int32 | 0x08 | 2 | AU/NZ
Reserved | [6 empty] | AU/NZ
wSettingEnableSignal | W/R | Reactive Power_Response for Volt_t |  | Uint16 |  | 1 | AU/NZ
wSettingLeadPoint | W/R | Lead point |  | Uint16 | 0x00 | 1 | AU/NZ
wSettingLaggPoint | W/R | Lag point |  | Uint16 | 0x01 | 1 | AU/NZ
wSettingVolt1 | W/R | Setting Volt1 |  | Uint16 | 0x02 | 1 | AU/NZ
wSettingVolt2 | W/R | Setting Volt2 |  | Uint16 | 0x03 | 1 | AU/NZ
wSettingVolt3 | W/R | Setting Volt3 |  | Uint16 | 0x04 | 1 | AU/NZ
wSettingVolt4 | W/R | Setting Volt4 |  | Uint16 | 0x05 | 1 | AU/NZ
Reserved | [6 empty] | AU/NZ
wSettingGenLimitEnableSignal | W/R | Active Power Response To Volt |  |  | 0x00 |  | AU/NZ
wSettingConsLimitEnableSignal | W/R | ConsLimitEnableSignal |  | Uint16 | 0x01 | 1 | AU/NZ
wSettingGenlimitPower | W/R | GenlimitPower |  | Uint16 | 0x02 | 1 | AU/NZ
wSettingVolt1 | W/R | Setting Volt1 |  | Uint16 | 0x03 | 1 | AU/NZ
wSettingVolt2 | W/R | Setting Volt2 |  | Uint16 | 0x04 | 1 | AU/NZ
wSettingVolt3 | W/R | Setting Volt3 |  | Uint16 | 0x05 | 1 | AU/NZ
wSettingVolt4 | W/R | Setting Volt4 |  | Uint16 | 0x06 | 1 | AU/NZ
Reserved |  |  |  | Uint16 | 0x07 | 1 | AU/NZ
Reserved | [6 empty] | AU/NZ
StartPoint_Freq | W/R | Power reduce for freq |  | Uint16 | 0x00 | 1 | AU/NZ
StopPoint_Freq | W/R | Stop point |  | Uint16 | 0x01 | 1 | AU/NZ
Power_RiseRate_Time | W/R | Power rise rate in time |  | Uint16 | 0x02 | 1 | AU/NZ
Reserved |  |  |  | Uint16 | 0x03 | 1 | AU/NZ
Reserved | [6 empty] | AU/NZ
StartPoint_Freq/charger power | W/R | Power reduce in charger side for freq |  | Uint16 | 0x00 | 1 | AU/NZ
StopPoint_Freq/charger power | W/R | Stop point |  | Uint16 | 0x01 | 1 | AU/NZ
Power_RiseRate_Time charger power | W/R | Power rise rate in time |  | Uint16 | 0x02 | 1 | AU/NZ
Reserved |  |  |  | Uint16 | 0x03 | 1 | AU/NZ
Reserved | [6 empty] | AU/NZ
PowerRate_Limit_Enable | W/R | Active power rate limit |  | Uint16 | 0x00 | 1 | AU/NZ
Prate_Rise_Time | W/R | Rise time |  | Uint16 | 0x01 | 1 | AU/NZ
Prate_Drop_Time | W/R | Drop time |  | Uint16 | 0x02 | 1 | AU/NZ
Reserved |  |  |  | Uint16 | 0x03 | 1 | AU/NZ
Fault Codes |  |  |  |  | INV Error Code
Fault | Bit | Discription |  |  | Byte number |  | Solo
TzProtectFault | BIT0 | Hardware protection |  |  | BYTE0 |  | Solo
MainsLostFault | BIT1 | Grid lost |  |  |  |  | Solo
GridVoltFault | BIT2 | Grid voltage fault |  |  |  |  | Solo
GridFreqFault | BIT3 | Grid Frequency fault |  |  |  |  | Solo
PLLLostFault | BIT4 | PLL lost,Phase lock failure |  |  |  |  | Solo
BusVoltFault | BIT5 | Bus voltage high fault |  |  |  |  | Solo
Reserved | BIT6 | Reserved |  |  |  |  | Solo
Inv_OCP_Fault | BIT7 | Invert over current protect |  |  |  |  | Solo
Dci_OCP_Fault | BIT8 | DCI over current protect |  |  | BYTE1 |  | Solo
ResidualCurrentFault | BIT9 | ResidualCurrentFault |  |  |  |  | Solo
PvVoltFault | BIT10 | Pv voltage high |  |  |  |  | Solo
Ac10Mins_Voltage_Fault | BIT11 | 10 minutes avg of grid voltage High ,10 minutes high voltage |  |  |  |  | Solo
IsolationFault | BIT12 | Isolation Fault |  |  |  |  | Solo
TemperatureOverFault | BIT13 | Temperature Over Fault |  |  |  |  | Solo
Fan1SpeedFault | BIT14 | Fan1Speed Fault |  |  |  |  | Solo
Fan2SpeedFault | BIT15 | Fan2Speed Fault |  |  |  |  | Solo
SpiCommsFault | BIT16 | SpiCommsFault Internal communication fault |  |  | BYTE2 |  | Solo
SciCommsFault | BIT17 | SciCommsFault serial port communication fault |  |  |  |  | Solo
CanCmmsFault | BIT18 | CanCmmsFault can, communication fault |  |  |  |  | Solo
InputConfigFault | BIT19 | InputConfigFault |  |  |  |  | Solo
EepromFault | BIT20 | EepromFault |  |  |  |  | Solo
RelayFault | BIT21 | RelayFault |  |  |  |  | Solo
SampleConsistenceFault | BIT22 | SampleConsistenceFault |  |  |  |  | Solo
ResidualCurrent_DeviceFault | BIT23 | ResidualCurrent_DeviceFault |  |  |  |  | Solo
Fan1_DeviceFault | BIT24 | Fan1_DeviceFault |  |  | BYTE3 |  | Solo
Fan2_DeviceFault | BIT25 | Fan2_DeviceFault |  |  |  |  | Solo
HCT_AC_DeviceFault | BIT26 | HCT_AC_DeviceFault |  |  |  |  | Solo
Overload Fault | BIT27 | Overload Fault |  |  |  |  | Solo
EPS OCP | BIT28 | EPS OCP EPS |  |  |  |  | Solo
DCI_DeviceFault | BIT29 | DCI_DeviceFault |  |  |  |  | Solo
Other Device Fault | BIT30 | Other Device Fault |  |  |  |  | Solo
Eps Relay Fault | BIT31 | Eps Relay Fault EPS |  |  |  |  | Solo
Solo
[5 empty] | Notice:low byte first when transmission,when,a bit is “1”,a fault has happened. |  | Solo
Solo
[5 empty] | Charger Error Code |  | Solo
Fault | Bit | Discription |  |  | Byte number |  | Solo
Charger_OCP_Boost | BITO | Boost over current BUS2 over current |  |  |  |  | Solo
Charger_OCP_Charger | BIT1 | Battery over current |  |  |  |  | Solo
Charger_OVP_BAT | BIT2 | Battery over volt |  |  |  |  | Solo
Charger_OVP_Boost | BIT3 | Boost over volt BUS2过 over voltage |  |  |  |  | Solo
Charger_OVP_BUS | BIT4 | Charger BUS over volt |  |  |  |  | Solo
Charger_FANFault | BIT5 | Charger_FANFault |  |  |  |  | Solo
EPS OverLoad | BIT6 | Charger EPS_OverLoad EPS over load |  |  | BYTE0 |  | Solo
Charger_Temp_High_ERR | BIT7 | Charger_Temp_High_ERR |  |  |  |  | Solo
Charger_Temp_Lower_ERR | BIT8 | Charger_Temp_Lower_ERR |  |  |  |  | Solo
Battery_awaken_Failed | BIT9 | Battery_awaken_Failed |  |  |  |  | Solo
Charger_Current_Sensor Boost Fault | BIT10 | Charger_Current_Sensor_Boost_Fault |  |  |  |  | Solo
Charger_Current_Sensor | BIT11 | Charger_Current_Sensor_Bat_Faul |  |  |  |  | Solo
Bat Fault |  | T Battery current sensor failure |  |  |  |  | Solo
Charger_EEPROM_WR_Fault | BIT12 | Charger_EEPROM_WR_Fault |  |  |  |  | Solo
Charger_UnRecover_FANXF |  | Inverter unrecoverable fan failure |  |  | BYTE1 |  | Solo
Charger_UnRecover_FANXFault | BIT13 | Charger_UnRecover_FANXFault |  |  |  |  | Solo
Spi ERR | BIT14 | Spi ERR ,inverter internal communication failure |  |  |  |  | Solo
Charger_CanERR | BIT15 | Charger_CanERR inverter can communication fault |  |  |  |  | Solo
Solo
[5 empty] | Manager Error Code |  | Solo
Fault | Bit | Discription |  |  | Byte number |  | Solo
DM9000 Error | BIT0 | Internet IC have trouble |  |  | BYTE0 |  | Solo
RtcError | BIT1 | Real Time IC have trouble |  |  |  |  | Solo
E2promError | BIT2 | EEPROM IC have trouble |  |  |  |  | Solo
|  | EMS storage fault |  |  |  |  | Solo
CanCommsError | BIT3 | Inter communication have trouble Ems Can communication fault |  |  |  |  | Solo
CT Error | BIT4 | CT or meter connection missing |  |  |  |  | Solo
Reserved | BIT5 | [5 empty] | Solo
Reserved | BIT6 | [5 empty] | Solo
Reserved | BIT7 | [5 empty] | Solo
Reserved | BIT8 | [5 empty] | Solo
Reserved | BIT9 | [5 empty] | Solo
Reserved | BIT10 | [5 empty] | Solo
Reserved | BIT11 | [5 empty] | Solo
Reserved | BIT12 | [5 empty] | Solo
Reserved | BIT13 |  |  |  | BYTE1 |  | Solo
Reserved | BIT14 | [5 empty] | Solo
Reserved | BIT15 | [5 empty] | Solo
Solo
[5 empty] | BMS Error Code |  | Solo
Fault | Bit | Discription |  |  | Byte number |  | Solo
BMS_Disconnected | BIT0 | Bms communication lost |  |  |  |  | Solo
BMS_Alarm | BIT1 | Bms alarm error bms |  |  |  |  | Solo
BMS_OverVoltage | BIT2 | Batter voltage too high bms Battery overvoltage |  |  |  |  | Solo
BMS_LowerVoltage | BIT3 | Batter voltage too low bms Battery undervoltage |  |  |  |  | Solo
BMS_ChargeOverCurrent | BIT4 | Batter charge current too high |  |  |  |  | Solo
|  | Bms Charging overcurrent |  |  |  |  | Solo
BMS_DishargeOverCurrent | BIT5 | Batter charge current too low |  |  | BYTE0 |  | Solo
|  | Bms Discharge overcurrent |  |  |  |  | Solo
BMS_TemHighWarning | BIT6 | Batter temperature too high |  |  |  |  | Solo
|  | Bms Over temperature |  |  |  |  | Solo
BMS_TemLowWarning | BIT7 | Batter temperature too low |  |  |  |  | Solo
|  | Bms temperature low |  |  |  |  | Solo
BMS_CellImblance | BIT8 | Bms Cell imbalance |  |  |  |  | Solo
Reserved | BIT9 | [5 empty] | Solo
Reserved | BIT10 | [5 empty] | Solo
Reserved | BIT11 | [5 empty] | Solo
Reserved | BIT12 | [5 empty] | Solo
Reserved | BIT13 |  |  |  | BYTE1 |  | Solo
Reserved | BIT14 | [5 empty] | Solo
Reserved | BIT15 | [5 empty] | Solo